## cover
|  |  |  | Doc. No. |  | TG - WSP - 100
Technical Guide
White Smoke Prevention
|  |  |  | Total | 6 | sheets with a cover
5
4
3
2
1 | 2016. 3. 1. | Updated. |  | S. J. Lee |  | LSJ | Lee
0 | 2002. 4. 5. | Originally Prepared. |  | S. J. Lee |  | LSJ | Lee
Rev. | Date | Description |  | Prepared |  | Reviewed | Approved
나 래 열 기 술
Narai Thermal Engineering Services ( NTES )
| Homepage | www.ntes.co.kr |  | E-mail |  | ntes@ntes.co.kr
NTES | [7 empty] | Narai Thermal engineering Services

## TOC
| Technical Guide : |  |  | Doc. No. | TG - WSP - 100
White Smoke Prevention |  |  |  | Date | 2016. 3. 1.
|  |  |  | Rev. | 0 | 1
|  |  |  | Sheet No. |  | 1 | of | 1
T a b l e of C o n t e n t s
|  | 1. | Psychrometric Process
|  | 2. | Reheating Method
|  | 3. | Dilution Method
|  | 4. | Dehumidifying Method
NTES | [8 empty] | Narai Thermal engineering Services

## 1
| Technical Guide : | [11 empty] | Doc. No. | TG - WSP - 100
White Smoke Prevention | [12 empty] | Date | 2016. 3. 1.
[13 empty] | Rev. | 0 | 1
[13 empty] | Sheet No. |  | 1 | of | 4
|  | 1. | Psychrometric Process
Psychrometric Chart
Humidity Ratio
W
Fog Region
Saturation Line
Dry Bulb Temperature
State of Most Gas discharged to a stack
State of Ambient Air
State of Dilution Air
[5 empty] | - |  |  | Condition Line
|  |  | White Smoke |  |  | ( | Fog | )
|  |  | Fog is generated in case the straight line | [5 empty] | - | crosses the saturation line.
The greater the area of intersection, the more intense the fog.
Prevention
Reheating Method
|  |  |  | Process |  | :
Dilution Method
|  |  |  | Process |  | :
↑
Dehumidifying Method
|  |  |  | Process |  | :
NTES | [17 empty] | Narai Thermal engineering Services
Note on AD4: Cell is filled !
1
1
2
3
4
5
1
1
7
2
3
6
7
1
1
1
2
3
5
6
4
4
7
4
5
6
1
7
1
7

## 2
| Technical Guide : | [13 empty] | Doc. No. |  | TG - WSP - 100
White Smoke Prevention | [14 empty] | Date |  | 2016. 3. 1.
[15 empty] | Rev. |  | 0 | 1
[15 empty] | Sheet No. |  |  | 2 | of | 4
|  | 2. | Reheating Method
Process
Humidity Ratio
|  |  | ma | [6 empty] | ma | [7 empty] | W1
|  |  | h1 |  |  |  | Q |  |  | h2
|  |  | W1 | [6 empty] | W2
|  |  | T1 | [6 empty] | T2
[6 empty] | Heater |  |  |  |  | Saturation Line
[11 empty] | Dry Bulb Temperature |  |  |  | T1 | T2
[15 empty] | 2 | 40
|  |  | Moist gas is heated to a higher temperature so that the condition line | [10 empty] | - | does not cross the saturation line.
|  |  | Heat and Mass Balance | [18 empty] | Fluid Name |  |  | Flue Gas | [5 empty] | Used
[22 empty] | Fluid Type |  |  | Gas Mixture | [5 empty] | Moist Air |  |  |  |  | Gas Mixture
|  |  | W2 | = | W1 | [19 empty] | Inlet |  | Outlet |  |  |  |  | Input | Inlet | Outlet |  | Inlet
[22 empty] | Flowrate, Total |  |  | 3000 |  | m3/h |  |  |  | Yes | volume% |  |  |  | - N/A - |  | volume% |  | volume% | weight%
|  |  | Q | = | ma | ( | h2 | - | h1 | ) | [12 empty] | Vapor |  | 3000 |  | 3000 |  |  |  | H2O | 0.69676 | 0.69676 | 0.69676 |  | H2O |  | 3.85 |  | *** | ***
[23 empty] | Liquid |  | 0 |  | 0 |  |  |  | N2 | 77.5423 | 77.5423 | 77.5423 |  | CO2 |  | 0 |  | *** | ***
[23 empty] | Condensate |  | 0 |  | 0 |  |  | kg/h | O2 | 20.8023 | 20.8023 | 20.8023 |  | N2 |  | 76 |  | *** | ***
|  |  | Sample Calculation | [18 empty] | Temperature |  |  | 2 |  | 40 |  |  | ℃ | Ar | 0.92752 | 0.92752 | 0.92752 |  | O2 |  | 20.15 |  | *** | ***
|  |  | Fluid Name | [6 empty] | Flue Gas | [11 empty] | Press. | Input / Gauge |  | 0 | 0 |  |  |  | mmH2O | CO2 | 0.031182 | 0.031182 | 0.031182 |  | SO2 |  | 0 |  | *** | ***
[10 empty] | Inlet |  | Outlet | [10 empty] | ΔP / Outlet, Input / Gauge |  |  | 0 | 0 |  | 0 | Gauge |  | 0 | 0 | 0 | [5 empty] | *** | ***
|  |  | Flowrate | [6 empty] | 3000 |  | 3414.3195 | m3/h | [8 empty] | Dew Point |  |  | 2 |  | 2 |  |  | ℃ |  | 0 | 0 | 0 | [5 empty] | *** | ***
|  |  | Temperature | [5 empty] | T1 | 2 | T2 | 40 | ℃ | [8 empty] | Molecular Weight |  |  | 28.8885 |  | 28.8885 |  |  |  |  | 0 | 0 | 0 | [5 empty] | *** | ***
|  |  | Pressure | [6 empty] | 0 |  | 0 | mmH2O | [8 empty] | Density | i / m / o |  | 1.2795 | 1.1969 |  | 1.1242 |  | kg/m3 |  | 0 | 0 | 0 | [5 empty] | *** | ***
|  |  | Relative Humidity | [6 empty] | 100 |  | 9.5605 | % | [11 empty] | 1.2889 |  | 1.2889 |  |  | kg/Nm3 |  | 0 | 0 | 0 | [5 empty] | *** | ***
|  |  | Humidity Ratio | [5 empty] | W1 | 0.004364 | W2 | 0.004364 | kg/kg.dry gas | [8 empty] | Flowrate, Total |  |  | 3838.4994 |  | 3838.4994 |  |  | kg/h | Total | 100 | 100 | 100 |  | Total |  | 100 |  | *** | ***
|  |  | Flowrate |  |  | Volumetric |  |  |  | 3000 |  | 3414.3195 | m3/h | [11 empty] | 3000 |  | 3414.3195 |  |  | m3/h | M. Weight | 28.8885 | 28.8885 | 28.8885 |  | M. Weight |  | ***
|  |  | Specific Volume | [6 empty] | 0.78497 |  | 0.89338 | m3/kg.dry gas | [8 empty] | Enthalpy |  |  | 0.48211 |  | 9.6468 |  |  | kcal/kg | Density | 1.2889 | 1.2889 | 1.2889 | kg/Nm3 | Density |  | *** |  | kg/Nm3
|  |  | Flowrate | [5 empty] | ma | 3821.8209 | ma | 3821.8209 | kg.dry gas/h | [8 empty] | Specific Heat |  | i / m / o | 0.24106 | 0.24116 |  | 0.24131 |  | kcal/kg.℃ | Dew Point |  | * SO2 -> SO3, % | 3 |  | Dew Point |  | * SO2 -> SO3, % |  | 3
|  |  | Enthalpy | [5 empty] | h1 | 0.48421 | h2 | 9.6889 | kcal/kg.dry gas | [10 empty] | Mean | 0.24105 |  | 0.24117 |  |  | kcal/kg.℃ |  | Water | 2 | 2 | ℃ |  | Water | *** |  | ℃
[10 empty] | 2.0273 |  | 40.5655 | kJ/kg.dry gas | [8 empty] | Heat Change |  |  | 35178.7266 |  |  |  |  | kcal/h |  | Sulfuric | 0 | 0 | ℃ |  | Sulfuric | *** |  | ℃
|  |  | Heat Load | [5 empty] | Q | 35178.7266 | / | 40.9055 | kcal/h / kW | [8 empty] | P S Y C H R O M E T R I C S | [8 empty] | Condensate
[22 empty] | Relative Humidity |  |  | 100 |  | 9.5605 |  |  | % | xcond |  | 0 | 0 |  |  |  | 적 용
|  |  | * Latent heat is not included in Enthalpy h1 and h2. | [18 empty] | xw |  |  | 0.0043451 |  | 0.0043451 |  |  | H2O wt Fraction | Flowrate |  | 0 | 0 | kg/h | Moist Air |  | Yes
[22 empty] | W |  |  | 0.004364 |  | 0.004364 |  |  | kg/kg.dry gas | [5 empty] | Temperature |  | 2 |  | ℃
[22 empty] | Density |  |  | 1.2739 |  | 1.1194 |  |  | kg.dry gas/m3 | [5 empty] | Pressure |  | 0 |  | kg/cm2.g
[22 empty] | Specific Volume |  |  | 0.78497 |  | 0.89338 |  |  | m3/kg.dry gas | [5 empty] | Relative Humidity |  | 100 |  | % | twbulb
[22 empty] | ma |  |  | 3821.8209 |  | 3821.8209 |  |  | kg.dry gas/h | [5 empty] | Dew Point |  | 2 |  | ℃ | 1.999
[22 empty] | ha |  |  | 0.48421 |  | 9.6889 |  |  | kcal/kg.dry gas | [5 empty] | Composition |  | volume% | weight% |  | Dry Air
[22 empty] | Heat Load |  |  | 35178.7266 |  |  |  |  | kcal/h | [5 empty] | H2O |  | 0.69676 | 0.43451 |  | 0
[36 empty] | N2 |  | 77.5423 | 75.1934 |  | 78.084
[36 empty] | O2 |  | 20.8023 | 23.042 |  | 20.9476
[36 empty] | Ar |  | 0.92752 | 1.2826 |  | 0.934
[36 empty] | CO2 |  | 0.031182 | 0.047504 |  | 0.0314
[36 empty] | Total |  | 100 | 100 |  | 99.997
NTES | [20 empty] | Narai Thermal engineering Services
Note on AD4: Cell is filled !
Note on AY46: 2 ~ 5
1
2
7
7
1
2

## 3
| Technical Guide : | [17 empty] | Doc. No. |  |  | TG - WSP - 100
White Smoke Prevention | [18 empty] | Date |  |  | 2016. 3. 1.
[19 empty] | Rev. |  |  | 0 | 1
[19 empty] | Sheet No. |  |  |  | 3 | of | 4
|  | 3. | Dilution Method
Process
Humidity Ratio
|  |  | ma1 | [6 empty] | ma3 | [12 empty] | W1
|  |  | h1 | [6 empty] | h3
|  |  | W1 | [6 empty] | W3
|  |  | T1 | [6 empty] | T3
W3
Saturation Line
ma2
[6 empty] | h2 | [16 empty] | W2
W2
[6 empty] | T2 | [6 empty] | Dry Bulb Temperature |  |  |  | T2 | T3 |  | T1
[17 empty] | 4 | 19.63 |  | 25
Dilution air is added to moist gas so that humidity ratio of the mixed gas is reduced.
|  |  | The condition line |  |  |  |  | - |  | shall not cross the saturation line.
[28 empty] | Fluid Name |  |  | Flue Gas | [5 empty] | Used
|  |  | Heat and Mass Balance | [24 empty] | Fluid Type |  |  | Gas Mixture | [5 empty] | Moist Air |  |  |  |  | Gas Mixture
[31 empty] | Inlet |  | Outlet |  |  |  |  | Input | Inlet | Outlet |  | Inlet
|  |  | ma1 |  | + | ma2 |  | = | ma3 | [18 empty] | Flowrate, Total |  |  | 25000 |  | m3/h |  |  |  | Yes | volume% |  |  |  | - N/A - |  | volume% |  | volume% | weight%
|  |  | ma1 | h1 | + | ma2 | h2 | = | ma3 | h3 | [18 empty] | Vapor |  | 25000 |  | 25000 |  |  |  | H2O | 1.5641 | 1.5641 | 1.5641 |  | H2O |  | 3.85 |  | *** | ***
|  |  | ma1 | W1 | + | ma2 | W2 | = | ma3 | W3 | [18 empty] | Liquid |  | 0 |  | 0 |  |  |  | N2 | 76.865 | 76.865 | 76.865 |  | CO2 |  | 0 |  | *** | ***
[29 empty] | Condensate |  | 0 |  | 0 |  |  | kg/h | O2 | 20.6206 | 20.6206 | 20.6206 |  | N2 |  | 76 |  | *** | ***
|  | -> | h2 | - | h3 | = | W2 | - | W3 | = | ma1 | [16 empty] | Temperature |  |  | 25 |  | 25 |  |  | ℃ | Ar | 0.91942 | 0.91942 | 0.91942 |  | O2 |  | 20.15 |  | *** | ***
|  |  | h3 | - | h1 |  | W3 | - | W1 |  | ma2 | [16 empty] | Press. | Input / Gauge |  | 0 | 0 |  |  |  | mmH2O | CO2 | 0.03091 | 0.03091 | 0.03091 |  | SO2 |  | 0 |  | *** | ***
[29 empty] | ΔP / Outlet, Input / Gauge |  |  | 0 | 0 |  | 0 | Gauge |  | 0 | 0 | 0 | [5 empty] | *** | ***
[28 empty] | Dew Point |  |  | 13.8639 |  | 13.8639 |  |  | ℃ |  | 0 | 0 | 0 | [5 empty] | *** | ***
|  |  | Sample Calculation | [24 empty] | Molecular Weight |  |  | 28.7935 |  | 28.7935 |  |  |  |  | 0 | 0 | 0 | [5 empty] | *** | ***
|  |  | Fluid Name | [6 empty] | Flue Gas |  |  |  | Ambient Air |  |  | Mixed Gas | [10 empty] | Density | i / m / o |  | 1.1769 | 1.1769 |  | 1.1769 |  | kg/m3 |  | 0 | 0 | 0 | [5 empty] | *** | ***
[10 empty] | Inlet |  |  |  | Inlet |  |  | Outlet | [13 empty] | 1.2846 |  | 1.2846 |  |  | kg/Nm3 |  | 0 | 0 | 0 | [5 empty] | *** | ***
|  |  | Flowrate | [6 empty] | 25000 |  |  |  | 8000 |  |  | 33000.8869 |  |  | m3/h | [6 empty] | 33000 | Flowrate, Total |  |  | 29422.8519 |  | 29422.8519 |  |  | kg/h | Total | 100 | 100 | 100 |  | Total |  | 100 |  | *** | ***
|  |  | Temperature | [5 empty] | T1 | 25 |  |  | T2 | 4 |  | T3 | 19.63 |  |  | ℃ | [10 empty] | 25000 |  | 25000 |  |  | m3/h | M. Weight | 28.7935 | 28.7935 | 28.7935 |  | M. Weight |  | ***
|  |  | Pressure | [6 empty] | 0 |  |  |  | 0 |  |  | 0 |  |  | mmH2O | [7 empty] | Enthalpy |  |  | 6.0557 |  | 6.0557 |  |  | kcal/kg | Density | 1.2846 | 1.2846 | 1.2846 | kg/Nm3 | Density |  | *** |  | kg/Nm3
|  |  | Relative Humidity | [6 empty] | 50 |  |  |  | 70.8 |  |  | 58.0241 |  |  | % | [7 empty] | Specific Heat |  | i / m / o | 0.2423 | 0.2423 |  | 0.2423 |  | kcal/kg.℃ | Dew Point |  | * SO2 -> SO3, % | 3 |  | Dew Point |  | * SO2 -> SO3, % |  | 3
|  |  | Humidity Ratio | [5 empty] | W1 | 0.0098831 |  |  | W2 | 0.0035559 |  | W3 | 0.0082506 |  |  | kg/kg.dry gas | [9 empty] | Mean | 0.24223 |  | 0.24223 |  |  | kcal/kg.℃ |  | Water | 13.8639 | 13.8639 | ℃ |  | Water | *** |  | ℃
|  |  | Flowrate |  |  | Volumetric |  |  |  | 25000 |  |  |  | 8000 |  |  | 33000.8869 |  |  | m3/h | [7 empty] | Heat Capacity |  |  | 178175.1056 |  | 178175.1056 |  |  | kcal/h |  | Sulfuric | 0 | 0 | ℃ |  | Sulfuric | *** |  | ℃
|  |  | Specific Volume | [6 empty] | 0.85808 |  |  |  | 0.78965 |  |  | 0.84045 |  |  | m3/kg.dry gas | [7 empty] | P S Y C H R O M E T R I C S | [8 empty] | Condensate
|  |  | Flowrate | [5 empty] | ma1 | 29134.9082 |  |  | ma2 | 10131.0492 |  | ma3 | 39265.9573 |  |  | kg.dry gas/h | [6 empty] | 39265.9573 | Relative Humidity |  |  | 50 |  |  |  |  | % | xcond |  | 0 | 0 |  |  |  | 적 용
|  |  | Enthalpy | [5 empty] | h1 | 6.1155 |  |  | h2 | 0.96701 |  | h3 | 4.7873 |  |  | kcal/kg.dry gas | [7 empty] | xw |  |  | 0.0097864 |  | 0.0097864 |  |  | H2O wt Fraction | Flowrate |  | 0 | 0 | kg/h | Moist Air |  | Yes
[10 empty] | 25.6045 |  |  |  | 4.0487 |  |  | 20.0436 |  |  | kJ/kg.dry gas | [7 empty] | W |  |  | 0.0098831 |  | 0.0098831 |  |  | kg/kg.dry gas | [5 empty] | Temperature |  | 25 |  | ℃
|  |  | Heat Capacity | [6 empty] | 178175.1056 |  |  |  | 9796.8221 |  |  | 187979.142 |  |  | kcal/h | [6 empty] | 187971.9277 | Density |  |  | 1.1654 |  | 1.1654 |  |  | kg.dry gas/m3 | [5 empty] | Pressure |  | 0 |  | kg/cm2.g
[28 empty] | Specific Volume |  |  | 0.85808 |  | 0.85808 |  |  | m3/kg.dry gas | [5 empty] | Relative Humidity |  | 50 |  | % | twbulb
|  |  | * Latent heat is not included in Enthalpy h1, h2 and h3. | [24 empty] | ma |  |  | 29134.9082 |  | 29134.9082 |  |  | kg.dry gas/h | [5 empty] | Dew Point |  | 13.8639 |  | ℃ | 17.888
[28 empty] | ha |  |  | 6.1155 |  | 6.1155 |  |  | kcal/kg.dry gas | [5 empty] | Composition |  | volume% | weight% |  | Dry Air
[28 empty] | Heat Capacity |  |  | 178175.1056 |  | 178175.1056 |  |  | kcal/h | [5 empty] | H2O |  | 1.5641 | 0.97864 |  | 0
[42 empty] | N2 |  | 76.865 | 74.7825 |  | 78.084
[42 empty] | O2 |  | 20.6206 | 22.9161 |  | 20.9476
[42 empty] | Ar |  | 0.91942 | 1.2756 |  | 0.934
[42 empty] | CO2 |  | 0.03091 | 0.047244 |  | 0.0314
[42 empty] | Total |  | 100 | 100 |  | 99.997
NTES | [25 empty] | Narai Thermal engineering Services
[11 empty] | Fluid Name |  |  | Mixed Gas | [6 empty] | Used | [6 empty] | Fluid Name |  |  | Ambient Air | [5 empty] | Used
[11 empty] | Fluid Type |  |  | Gas Mixture | [6 empty] | 0 | [6 empty] | Fluid Type |  |  | Gas Mixture | [5 empty] | Moist Air |  |  |  |  | Gas Mixture
[14 empty] | Inlet |  | Outlet | [5 empty] | Input | Inlet | Outlet | [6 empty] | Inlet |  | Outlet |  |  |  |  | Input | Inlet | Outlet |  | Inlet
[11 empty] | Flowrate, Total |  |  | 33000.8869 |  | m3/h |  |  |  |  | Yes | volume% | [5 empty] | Flowrate, Total |  |  | 8000 |  | m3/h |  |  |  | Yes | volume% |  |  |  | - N/A - |  | volume% |  | volume% | weight%
[12 empty] | Vapor |  | 33000.8869 |  | 33000.8869 |  |  |  |  | H2O | 1.3092 | 1.3092 | 1.3092 |  |  |  |  | Vapor |  | 8000 |  | 8000 |  |  |  | H2O | 0.56846 | 0.56846 | 0.56846 |  | H2O |  | 3.85 |  | *** | ***
[12 empty] | Liquid |  | 0 |  | 0 |  |  |  |  | N2 | 77.0641 | 77.0641 | 77.0641 |  |  |  |  | Liquid |  | 0 |  | 0 |  |  |  | N2 | 77.6425 | 77.6425 | 77.6425 |  | CO2 |  | 0 |  | *** | ***
[7 empty] | Heat Capacity |  |  |  |  | Condensate |  | 0 |  | 0 |  |  | kg/h |  | O2 | 20.674 | 20.674 | 20.674 |  |  |  |  | Condensate |  | 0 |  | 0 |  |  | kg/h | O2 | 20.8291 | 20.8291 | 20.8291 |  | N2 |  | 76 |  | *** | ***
[7 empty] | 187971.9277 |  |  | -> | Temperature |  |  | 19.63 |  | 19.63 |  |  | ℃ |  | Ar | 0.9218 | 0.9218 | 0.9218 |  |  |  | Temperature |  |  | 4 |  | 4 |  |  | ℃ | Ar | 0.92872 | 0.92872 | 0.92872 |  | O2 |  | 20.15 |  | *** | ***
[11 empty] | Press. | Input / Gauge |  | 0 | 0 |  |  |  | mmH2O |  | CO2 | 0.03099 | 0.03099 | 0.03099 |  |  |  | Press. | Input / Gauge |  | 0 | 0 |  |  |  | mmH2O | CO2 | 0.031222 | 0.031222 | 0.031222 |  | SO2 |  | 0 |  | *** | ***
[12 empty] | ΔP / Outlet, Input / Gauge |  |  | 0 | 0 |  | 0 | Gauge |  |  | 0 | 0 | 0 |  |  |  |  | ΔP / Outlet, Input / Gauge |  |  | 0 | 0 |  | 0 | Gauge |  | 0 | 0 | 0 | [5 empty] | *** | ***
[11 empty] | Dew Point |  |  | 11.1547 |  | 11.1547 |  |  | ℃ |  |  | 0 | 0 | 0 |  |  |  | Dew Point |  |  | - N/A - |  | - N/A - |  |  | ℃ |  | 0 | 0 | 0 | [5 empty] | *** | ***
[11 empty] | Molecular Weight |  |  | 28.8214 |  | 28.8214 | [5 empty] | 0 | 0 | 0 |  |  |  | Molecular Weight |  |  | 28.9025 |  | 28.9025 |  |  |  |  | 0 | 0 | 0 | [5 empty] | *** | ***
[11 empty] | Density | i / m / o |  | 1.1997 | 1.1997 |  | 1.1997 |  | kg/m3 |  |  | 0 | 0 | 0 |  |  |  | Density | i / m / o |  | 1.2709 | 1.2709 |  | 1.2709 |  | kg/m3 |  | 0 | 0 | 0 | [5 empty] | *** | ***
[14 empty] | 1.2859 |  | 1.2859 |  |  | kg/Nm3 |  |  | 0 | 0 | 0 | [6 empty] | 1.2895 |  | 1.2895 |  |  | kg/Nm3 |  | 0 | 0 | 0 | [5 empty] | *** | ***
[7 empty] | 39589.9257 |  |  | -> | Flowrate, Total |  |  | 39589.9257 |  | 39589.9257 |  |  | kg/h |  | Total | 100 | 100 | 100 |  |  |  | Flowrate, Total |  |  | 10167.0739 |  | 10167.0739 |  |  | kg/h | Total | 100 | 100 | 100 |  | Total |  | 100 |  | *** | ***
[14 empty] | 33000.8869 |  | 33000.8869 |  |  | m3/h |  | M. Weight | 28.8214 | 28.8214 | 28.8214 | [6 empty] | 8000 |  | 8000 |  |  | m3/h | M. Weight | 28.9025 | 28.9025 | 28.9025 |  | M. Weight |  | ***
[11 empty] | Enthalpy |  |  | 4.7482 |  | 4.7482 |  |  | kcal/kg |  | Density | 1.2859 | 1.2859 | 1.2859 | kg/Nm3 |  |  | Enthalpy |  |  | 0.96358 |  | 0.96358 |  |  | kcal/kg | Density | 1.2895 | 1.2895 | 1.2895 | kg/Nm3 | Density |  | *** |  | kg/Nm3
[11 empty] | Specific Heat |  | i / m / o | 0.24194 | 0.24194 |  | 0.24194 |  | kcal/kg.℃ |  | Dew Point |  | * SO2 -> SO3, % | 3 |  |  |  | Specific Heat |  | i / m / o | 0.24091 | 0.24091 |  | 0.24091 |  | kcal/kg.℃ | Dew Point |  | * SO2 -> SO3, % | 3 |  | Dew Point |  | * SO2 -> SO3, % |  | 3
[13 empty] | Mean | 0.24188 |  | 0.24188 |  |  | kcal/kg.℃ |  |  | Water | 11.1547 | 11.1547 | ℃ |  |  |  |  | Mean | 0.2409 |  | 0.2409 |  |  | kcal/kg.℃ |  | Water | - N/A - | - N/A - | ℃ |  | Water | *** |  | ℃
[11 empty] | Heat Capacity |  |  | 187979.142 |  | 187979.142 |  |  | kcal/h |  |  | Sulfuric | 0 | 0 | ℃ |  |  | Heat Capacity |  |  | 9796.8221 |  | 9796.8221 |  |  | kcal/h |  | Sulfuric | 0 | 0 | ℃ |  | Sulfuric | *** |  | ℃
[11 empty] | P S Y C H R O M E T R I C S | [9 empty] | Condensate | [6 empty] | P S Y C H R O M E T R I C S | [8 empty] | Condensate
[11 empty] | Relative Humidity |  |  | 58.0241 |  |  |  |  | % |  | xcond |  | 0 | 0 |  |  |  | Relative Humidity |  |  | 70.8 |  |  |  |  | % | xcond |  | 0 | 0 |  |  |  | 적 용
[11 empty] | xw |  |  | 0.0081831 |  | 0.0081831 |  |  | H2O wt Fraction |  | Flowrate |  | 0 | 0 | kg/h |  |  | xw |  |  | 0.0035433 |  | 0.0035433 |  |  | H2O wt Fraction | Flowrate |  | 0 | 0 | kg/h | Moist Air |  | Yes
[11 empty] | W |  |  | 0.0082506 |  | 0.0082506 |  |  | kg/kg.dry gas | [8 empty] | W |  |  | 0.0035559 |  | 0.0035559 |  |  | kg/kg.dry gas | [5 empty] | Temperature |  | 4 |  | ℃
[11 empty] | Density |  |  | 1.1898 |  | 1.1898 |  |  | kg.dry gas/m3 | [8 empty] | Density |  |  | 1.2664 |  | 1.2664 |  |  | kg.dry gas/m3 | [5 empty] | Pressure |  | 0 |  | kg/cm2.g
[7 empty] | 39265.9573 |  |  | -> | Specific Volume |  |  | 0.84045 |  | 0.84045 |  |  | m3/kg.dry gas | [8 empty] | Specific Volume |  |  | 0.78965 |  | 0.78965 |  |  | m3/kg.dry gas | [5 empty] | Relative Humidity |  | 70.8 |  | % | twbulb
[11 empty] | ma |  |  | 39265.9573 |  | 39265.9573 |  |  | kg.dry gas/h | [8 empty] | ma |  |  | 10131.0492 |  | 10131.0492 |  |  | kg.dry gas/h | [5 empty] | Dew Point |  | - N/A - |  | ℃ | 2.004
[11 empty] | ha |  |  | 4.7873 |  | 4.7873 |  |  | kcal/kg.dry gas | [8 empty] | ha |  |  | 0.96701 |  | 0.96701 |  |  | kcal/kg.dry gas | [5 empty] | Composition |  | volume% | weight% |  | Dry Air
[11 empty] | Heat Capacity |  |  | 187979.142 |  | 187979.142 |  |  | kcal/h | [8 empty] | Heat Capacity |  |  | 9796.8221 |  | 9796.8221 |  |  | kcal/h | [5 empty] | H2O |  | 0.56846 | 0.35433 |  | 0
[42 empty] | N2 |  | 77.6425 | 75.254 |  | 78.084
[42 empty] | O2 |  | 20.8291 | 23.0605 |  | 20.9476
[42 empty] | Ar |  | 0.92872 | 1.2836 |  | 0.934
[42 empty] | CO2 |  | 0.031222 | 0.047542 |  | 0.0314
[42 empty] | Total |  | 100 | 100 |  | 99.997
Note on AD4: Cell is filled !
Note on AY46: 2 ~ 5
Note on AY84: 2 ~ 5
1
3
7
7
1
3
2

## 4
| Technical Guide : | [18 empty] | Doc. No. |  |  | TG - WSP - 100
White Smoke Prevention | [19 empty] | Date |  |  | 2016. 3. 1.
[20 empty] | Rev. |  |  | 0 | 1
[20 empty] | Sheet No. |  |  |  | 4 | of | 4
|  | 4. | Dehumidifying Method
Process
Humidity Ratio
|  |  | ma | [7 empty] | ma | [12 empty] | W1
|  |  | h1 |  |  | Q |  |  |  |  | h2
|  |  | W1 | [7 empty] | W2
|  |  | T1 | [7 empty] | T2
[8 empty] | hs | [15 empty] | W3
[7 empty] | Cooler | mw |  |  |  |  | Saturation Line | [10 empty] | W2
hw
[13 empty] | Dry Bulb Temperature |  |  | T2 |  |  | T3 |  | Td | T1 | [8 empty] | Ambient Air |  |  | 접점 1 |  | 접점 2
[16 empty] | 19.67 |  |  | 29.671 |  | 42.9859 | 50 | [8 empty] | Temp. | 5 | ℃ | 19.67 | ℃ | 29.671 | ℃
[31 empty] | RH | 30 | %
|  |  | Moist gas is cooled below the dew point so that moisture is condensed and removed. | [27 empty] | Fogging occurs !
|  |  | State |  | is the Ambient Air state.
|  |  | State |  | is the point where the condition line | [7 empty] | - |  | crosses the saturation line. | [12 empty] | Fluid Name |  |  | Flue Gas | [6 empty] | Used
|  |  | State |  | is the point where state | [5 empty] | changes and become a saturated. | [16 empty] | Fluid Type |  |  | Gas Mixture | [6 empty] | Gas Mixture |  |  |  |  | Gas Mixture
|  |  | Ideal process |  |  | : | [24 empty] | Inlet |  |  | Outlet |  |  |  |  | Input | Inlet | Outlet |  | Inlet
[10 empty] | Cooling |  |  | Condensing | [14 empty] | Flowrate, Total |  |  | 17000 |  |  | m3/h |  |  |  | Yes | volume% |  |  |  | Yes |  | volume% |  | volume% | weight%
|  |  | Actual process |  |  | : | [22 empty] | Vapor |  | 17000 |  |  | 14425.1691 |  |  |  | H2O | 8.5309 | 8.5309 | 2.2619 |  | H2O |  | 8.53 |  | 8.5309 | 5.4828
[10 empty] | Cooling +Condensing |  |  | Condensing | [15 empty] | Liquid | [8 empty] | N2 | 71.4271 | 71.4271 | 76.3225 |  | N2 |  | 71.42 |  | 71.4271 | 71.3838
[29 empty] | Condensate |  | 0 |  |  | 730.2918 |  |  | kg/h | O2 | 19.1619 | 19.1619 | 20.4752 |  | O2 |  | 19.16 |  | 19.1619 | 21.8748
|  |  | Heat and Mass Balance | [24 empty] | Temperature |  |  | 50 |  |  | 19.67 |  | 19.67 | ℃ | CO2 | 0.030003 | 0.030003 | 0.032059 |  | CO2 |  | 0.03 |  | 0.030003 | 0.047107
[28 empty] | Press. | Input / Gauge |  | 0 |  | 0 |  |  |  | mmH2O | SO2 | 0 | 0 | 0 |  | SO2 |  | 0 |  | 0 | 0
|  |  | ma | h1 | = | ma | h2 | + | Q | + | mw | hw | [16 empty] | ΔP / Outlet, Input / Gauge |  |  |  | 0 | 0 |  | 0 | Gauge | Ar | 0.85009 | 0.85009 | 0.90835 |  | Ar |  | 0.85 |  | 0.85009 | 1.2115
|  |  | ma | W1 | = | ma | W2 |  |  | + | mw | [16 empty] | Dew Point |  |  | 42.9859 |  |  | 19.67 |  |  | ℃ |  | 0 | 0 | 0 | [5 empty] | 0 | 0
[28 empty] | Molecular Weight |  |  | 28.0304 |  |  | 28.7168 |  |  |  |  | 0 | 0 | 0 | [5 empty] | 0 | 0
|  | -> | mw | = | ma | ( | W1 | - | W2 | ) | [17 empty] | Density |  |  | 1.0571 |  |  | 1.1951 |  |  | kg/m3 |  | 0 | 0 | 0 | [5 empty] | 0 | 0
|  |  | Q | = | ma | [ | ( | h1 | - | h2 | ) | + | ( | W1 | - | W2 | ) ( | hs | - | hw | ) | ] | [8 empty] | 1.2506 |  |  | 1.2812 |  |  | kg/Nm3 |  | 0 | 0 | 0 | [5 empty] | 0 | 0
[28 empty] | Flowrate, excl. Condensate |  |  | 17970.4603 |  |  | 17240.1685 |  |  | kg/h | Total | 100 | 100 | 100 |  | Total |  | 99.99 |  | 100 | 100
|  |  | Sample Calculation | [27 empty] | 17000 |  |  | 14425.1691 |  |  | m3/h | M. Weight | 28.0304 | 28.0304 | 28.7168 |  | M. Weight |  | 28.0304
|  |  | Fluid Name | [6 empty] | Flue Gas | [20 empty] | 14369.6426 |  |  | 13456.1674 |  |  | Nm3/h | Density | 1.2506 | 1.2506 | 1.2812 | kg/Nm3 | Density |  | 1.2506 |  | kg/Nm3
[10 empty] | Inlet |  |  |  | Outlet | [13 empty] | Enthalpy |  |  | 12.5836 |  |  | 4.7821 |  |  | kcal/kg | Dew Point |  | * SO2 -> SO3, % | 3 |  | Dew Point |  | * SO2 -> SO3, % |  | 3
|  |  | Flowrate | [6 empty] | 17000 |  |  |  | 14416.3738 |  |  | m3/h | [10 empty] | Specific Heat |  |  | 0.25218 |  |  | 0.24318 |  |  | kcal/kg.℃ |  | Water | 42.9859 | 19.67 | ℃ |  | Water | 42.9859 |  | ℃
|  |  | Temperature | [5 empty] | T1 | 50 |  |  | T2 | 19.67 |  |  | ℃ | [12 empty] | Mean | 0.25167 |  |  | 0.24311 |  |  | kcal/kg.℃ |  | Sulfuric | 0 | 0 | ℃ |  | Sulfuric | 0 |  | ℃
|  |  | Pressure | [6 empty] | 0 |  |  |  | 0 |  |  | mmH2O | [10 empty] | Heat Change |  |  | -140197.594 | [5 empty] | kcal/h | Condensate
|  |  | Relative Humidity | [6 empty] | 69.9838 |  |  |  | 100 |  |  | % | [10 empty] | P S Y C H R O M E T R I C S | [9 empty] | yw_cond |  | 0 | 0.06269 |  |  |  | 적 용
|  |  | Humidity Ratio | [5 empty] | W1 | 0.058008 |  |  | W2 | 0.014394 |  |  | kg/kg.dry gas | [10 empty] | Relative Humidity |  |  | 69.9838 |  |  | 100 |  |  | % | Flowrate |  | 0 | 900.8326 | Nm3/h | Moist Air |  | No
|  |  | Flowrate |  |  | Volumetric |  |  |  | 17000 |  |  |  | 14416.3738 |  |  | m3/h | [10 empty] | xw |  |  | 0.054828 |  |  | 0.01419 |  |  | H2O wt Fraction | xw_cond |  | 0 | 0.040638 |  | Temperature |  | 50 |  | ℃
|  |  | Specific Volume | [6 empty] | 1.0009 |  |  |  | 0.84876 |  |  | m3/kg.dry gas | [10 empty] | W |  |  | 0.058008 |  |  | 0.014394 |  |  | kg/kg.dry gas | Flowrate |  | 0 | 730.2918 | kg/h | Pressure |  | 0 |  | kg/cm2.g
|  |  | Flowrate | [5 empty] | ma | 16985.1763 |  |  | ma | 16985.1763 |  |  | kg.dry gas/h | [10 empty] | Density |  |  | 0.99913 |  |  | 1.1782 |  |  | kg.dry gas/m3 |  | yw_inet | 0.085309 | 0.085309 |  | Relative Humidity |  | 70 |  | % | twbulb
[13 empty] | mw | 740.8035 |  |  | kg/h | [10 empty] | Specific Volume |  |  | 1.0009 |  |  | 0.84876 |  |  | m3/kg.dry gas |  | yw_sat | 0.1219 | 0.022619 |  | Dew Point |  | 42.9903 |  | ℃ | 43.834
|  |  | Enthalpy | [5 empty] | h1 | 13.3136 |  |  | h2 | 4.8509 |  |  | kcal/kg.dry gas | [10 empty] | ma |  |  | 16985.1763 |  |  | 16995.5388 |  |  | kg.dry gas/h |  | xw_inlet | 0.054828 | 0.054828 |  | Composition |  | volume% | weight% |  | Dry Air
[9 empty] | hs | 605.9208 |  |  | hw | 19.7363 |  |  | kcal/kg | [10 empty] | ha |  |  | 13.3136 |  |  | 4.8509 |  |  | kcal/kg.dry gas |  | xw_sat | 0.07948 | 0.01419 |  | H2O |  | 8.5328 | 5.4841 |  | 0
|  |  | Heat Load | [5 empty] | Q | -577987.6964 |  |  | / | -672.0787 |  |  | kcal/h / kW | [10 empty] | hs / hw at Dew Point |  |  | 605.9208 |  |  | 19.7363 |  |  | kcal/kg |  | w_sat | 0.086342 | 0.014394 |  | N2 |  | 71.4234 | 71.3799 |  | 78.084
[28 empty] | Heat Load |  |  | -577987.6964 | [5 empty] | kcal/h | [5 empty] | O2 |  | 19.1608 | 21.8734 |  | 20.9476
|  |  | * Latent heat is not included in Enthalpy h1 and h2. | [39 empty] | Ar |  | 0.85433 | 1.2176 |  | 0.934
[43 empty] | CO2 |  | 0.028722 | 0.045095 |  | 0.0314
[43 empty] | Total |  | 100 | 100 |  | 99.997
NTES | [26 empty] | Narai Thermal engineering Services
[10 empty] | 55.7413 |  |  |  | 20.3097 |  |  | kJ/kg.dry gas
Note on AD4: Cell is filled !
Note on AY46: 2 ~ 5
1
7
2
1
7
1
3
2
3
1
2
3
1
4
1
4
2
7
2
3

## 0
| Technical Guide : |  |  | Doc. No. | TG - WSP - 100
White Smoke Prevention |  |  |  | Date | 2011. 1. 5.
|  |  |  | Rev. | 0
|  |  |  | Sheet No. |  | 0 | of | 4
|  | 0. | Aaaaaa
NTES | [8 empty] | Narai Thermal engineering Services
Note on AD4: Cell is filled !
1