## Condenser
C A L C U L A T I O N o f T H E R M A L E X P A N S I O N
1 | Project |  |  | Songdo CCPP | [10 empty] | Job No. |  | 060353
2 | Client |  |  | Incheon Energy Co., Ltd. | [10 empty] | Doc. No. |  | CAL - TEXP - 100 |  |  |  |  | Steam
3 | Contractor |  |  | Daelim Industrial Co., Ltd. | [10 empty] | Date |  | 2015. 1. 10. |  |  |  |  | Sat.
4 | [14 empty] | Revision |  | 0 |  |  |  |  | 5 | kg/cm2.g | 158.286 | < Tsat.
5 | Service of Unit |  |  | DH Heater #1 | [10 empty] | Item No. |  | 111-M-HE-001 |  |  |  |  | 158.286 |  | 250 | < TSH
6 | D E S I G N D A T A
7 | Shell Side | [9 empty] | Tube Side | [10 empty] | Shell Side |  |  | Tube Side
8 | Fluid Name |  |  |  |  | Steam |  |  |  |  | Fluid Name |  |  |  |  | DH Water |  |  |  |  | Fluid Kind | Saturated
9 | Inlet Press. |  |  |  |  | 5 |  |  | kg/cm2.g |  | Inlet Temp. |  |  | Ti | = | 65 |  |  | ℃ |  | Fluid in DB | H2O
10 | Inlet Temp. |  |  | To | = | 158.286 |  |  | ℃ |  | Outlet Temp. |  |  | To | = | 90 |  |  | ℃
11 | Shell Material |  |  |  |  | A 283-C |  |  |  |  | Channel Material |  |  |  |  | A 516-70 |  |  |  |  | Material | ASTM
12 | Ambinet Temp. |  |  | Ta | = | 21 |  |  | ℃ | [12 empty] | plate |  |  | plate
13 | A S S U M P T I O N f o r C A L C U L A T I O N
14 | 1. | Saddle expansion is not considered.
15 | 2. | Origin of coordinate is located at the point, where there is no movement.
16 | 3. | Mean coefficient of thermal expansion values are from TEMA, Table D-11 M.
17 | C A L C U L A T I O N R E S U L T
18 |  |  | Δ ( | -2.8346 | 1.7387 | ) |  |  |  | Δ ( | 4.3303 | 4.3823 | ) |  |  | Δ ( | 12.8178 | 4.3823 | )
19 |  |  | N5 ( | -2100 | 2482 | ) |  |  |  | N1 ( | 2500 | 2530 | ) |  |  | N2 ( | 7400 | 2530 | )
20 |  |  |  | N5 | [6 empty] | N1 | [5 empty] | N2
21 | 17 | t | 250 | [9 empty] | 300 | 15 | t |  |  |  | 300
22 | ID | OD | [6 empty] | 2500 |  |  |  |  | ID | OD |  | 1500
23 | 2200 | 2234 | [11 empty] | 2200 | 2230
24 |  |  |  |  | 900 | 1200
25
26 | [8 empty] | 4000
27
28 |  |  | 250 | [9 empty] | 300
29 |  |  |  | N4 | [6 empty] | N3
30 |  |  | N4 ( | -2100 | -252 | ) |  |  |  | N3 ( | 4000 | -300 | ) |  |  | SS
31 |  |  | Δ ( | -2.5543 | -0.13214 | ) |  |  |  | Δ ( | 6.9285 | -0.51964 | ) |  | SS ( | 5900 | 0 | )
32 | [10 empty] | 5900 |  |  |  | Δ ( | 10.2196 | 0 | )
33
34 | C A L C U L A T I O N D E T A I L
35 | [7 empty] | Shell Material |  |  |  |  | Channel Material
36 | Mean Coeff. of Thermal Expansion | [5 empty] | αT | at | Oper. Temp. |  | 12.4809 |  | at | Inlet Temp. |  | 11.8764 |  | mm / mm ℃ / 10^6
37 | [12 empty] | at | Outlet Temp. |  | 12.0384 |  | mm / mm ℃ / 10^6
38 | [6 empty] | αTa | at | Ambient Temp. |  | 11.5913 |  | at | Ambient Temp. |  | 11.5913 |  | mm / mm ℃ / 10^6
39 | Calculation Formula :
40 |  | Δ | = | L x ( αT x T - αTa x Ta ) | [5 empty] | Where, | L | Length |  | mm | T | Temp., Oper, Inlet or Outlet |  |  |  | ℃
41 | [10 empty] | Δ | Elongation |  | mm
42 | Point | SS | Δx | = | 5900 |  | x ( | 12.4809 | x | 158.286 | - | 11.5913 | x | 21 | ) / 10^6 |  | = | 10.2196 |  | mm
43 |  |  | Δz | = | 0 |  | x ( | 12.4809 | x | 158.286 | - | 11.5913 | x | 21 | ) / 10^6 |  | = | 0 |  | mm
44 | Point | N1 | Δx | = | 2500 |  | x ( | 12.4809 | x | 158.286 | - | 11.5913 | x | 21 | ) / 10^6 |  | = | 4.3303 |  | mm
45 |  |  | Δz | = | 2530 |  | x ( | 12.4809 | x | 158.286 | - | 11.5913 | x | 21 | ) / 10^6 |  | = | 4.3823 |  | mm
46 | Point | N2 | Δx | = | 7400 |  | x ( | 12.4809 | x | 158.286 | - | 11.5913 | x | 21 | ) / 10^6 |  | = | 12.8178 |  | mm
47 |  |  | Δz | = | 2530 |  | x ( | 12.4809 | x | 158.286 | - | 11.5913 | x | 21 | ) / 10^6 |  | = | 4.3823 |  | mm
48 | Point | N3 | Δx | = | 4000 |  | x ( | 12.4809 | x | 158.286 | - | 11.5913 | x | 21 | ) / 10^6 |  | = | 6.9285 |  | mm
49 |  |  | Δz | = | -300 |  | x ( | 12.4809 | x | 158.286 | - | 11.5913 | x | 21 | ) / 10^6 |  | = | -0.51964 |  | mm
50 |  |  | Δxs | = | -1200 |  | x ( | 12.4809 | x | 158.286 | - | 11.5913 | x | 21 | ) / 10^6 |  | = | -2.0786 |  | mm
51 | Point | N4 | Δxc | = | -900 |  | x ( | 11.8764 | x | 65 | - | 11.5913 | x | 21 | ) / 10^6 |  | = | -0.47569 |  | mm
52 |  |  | Δx | = | Δxs | + | Δxc | [9 empty] | = | -2.5543 |  | mm
53 |  |  | Δz | = | -250 |  | x ( | 11.8764 | x | 65 | - | 11.5913 | x | 21 | ) / 10^6 |  | = | -0.13214 |  | mm
54 |  |  | Δxs | = | -1200 |  | x ( | 12.4809 | x | 158.286 | - | 11.5913 | x | 21 | ) / 10^6 |  | = | -2.0786 |  | mm
55 |  |  | Δxc | = | -900 |  | x ( | 12.0384 | x | 90 | - | 11.5913 | x | 21 | ) / 10^6 |  | = | -0.75604 |  | mm
56 | Point | N5 | Δx | = | Δxs | + | Δxc | [9 empty] | = | -2.8346 |  | mm
57 |  |  | Δzci | = | 1117 |  | x ( | 11.8764 | x | 65 | - | 11.5913 | x | 21 | ) / 10^6 |  | = | 0.59039 |  | mm
58 |  |  | Δzco | = | 1367 |  | x ( | 12.0384 | x | 90 | - | 11.5913 | x | 21 | ) / 10^6 |  | = | 1.1483 |  | mm
59 |  |  | Δz | = | Δzci | + | Δzco | [9 empty] | = | 1.7387 |  | mm
60 | Notes
61 | *1)
62 | *2)
63 | *3)
| NTES | [18 empty] | Narai Thermal Enginering Services
"Z"
"X"
Origin of Coordinate
Fixed Side
Sliding Side

## _Drain Cooler
C A L C U L A T I O N o f T H E R M A L E X P A N S I O N
1 | Project |  |  | Gangnam CCPP | [10 empty] | Job No. |  | Later
2 | Client |  |  | KDHC | [10 empty] | Doc. No. |  | CAL - TEXP - 100 |  |  |  |  | Steam
3 | Contractor |  |  | Won Plant Co., Ltd. | [10 empty] | Date |  | 2015. 1. 10. |  |  |  |  | Sat.
4 | [14 empty] | Revision |  | 0 |  |  |  |  | 5 | kg/cm2.g | 158.286 | < Tsat.
5 | Service of Unit |  |  | Turbine By-pass H/E | [10 empty] | Item No. |  | 112-M-HE-003 |  |  |  |  | 158.286 |  | 250 | < TSH
6 | D E S I G N D A T A
7 | Shell Side | [9 empty] | Tube Side | [10 empty] | Shell Side |  |  | Tube Side
8 | Fluid Name |  |  |  |  | Steam |  |  |  |  | Fluid Name |  |  |  |  | DH Water |  |  |  |  | Fluid Kind | Saturated
9 | Inlet Press. |  |  |  |  | 5 |  |  | kg/cm2.g |  | Inlet Temp. |  |  | Ti | = | 65 |  |  | ℃ |  | Fluid in DB | H2O
10 | Inlet Temp. |  |  | Ti | = | 158.286 |  |  | ℃ |  | Outlet Temp. |  |  | To | = | 105 |  |  | ℃
11 | Shell Material |  |  |  |  | A 516-70 |  |  |  |  | Channel Material |  |  |  |  | A 516-70 |  |  |  |  | Material | ASTM
12 | Ambinet Temp. |  |  | Ta | = | 10 |  |  | ℃ | [12 empty] | plate |  |  | plate
13 | A S S U M P T I O N f o r C A L C U L A T I O N
14 | 1. | Saddle expansion is not considered.
15 | 2. | Origin of coordinate is located at the point, where there is no movement.
16 | 3. | Mean coefficient of thermal expansion values are from TEMA, Table D-11 M.
17 | C A L C U L A T I O N R E S U L T
18 |  |  | Δ ( | -2.4972 | 1.8276 | ) |  |  |  | Δ ( | 2.6045 | 3.9514 | ) |  |  | Δ ( | 6.5112 | 3.9514 | )
19 |  |  | N5 ( | -1610 | 2027 | ) |  |  |  | N1 ( | 1400 | 2124 | ) |  |  | N2 ( | 3500 | 2124 | )
20 |  |  |  | N5 | [6 empty] | N1 | [5 empty] | N2
21 | 15 | t | 300 | [9 empty] | 300 | 12 | t |  |  |  | 300
22 | ID | OD | [6 empty] | 1400 |  |  |  |  | ID | OD |  | 1000
23 | 1600 | 1630 | [11 empty] | 1800 | 1824
24 |  |  |  |  | 710 | 900
25
26 | [6 empty] | 530
27
28 |  |  | 300 |  |  | 300
29 |  |  |  | N4 |  |  | N3
30 |  |  | N4 ( | -1610 | -203 | ) N3 ( | -530 | -300 | ) | [6 empty] | SS
31 |  |  | Δ ( | -2.1406 | -0.19703 | ) Δ ( | -0.98599 | -0.55811 | ) | [5 empty] | SS ( | 2500 | 0 | )
32 | [10 empty] | 2500 |  |  |  | Δ ( | 4.6509 | 0 | )
33
34 | C A L C U L A T I O N D E T A I L
35 | [7 empty] | Shell Material |  |  |  |  | Channel Material
36 | Mean Coeff. of Thermal Expansion | [5 empty] | αT | at | Oper. Temp. |  | 12.4809 |  | at | Inlet Temp. |  | 11.8764 |  | mm / mm ℃ / 10^6
37 | [12 empty] | at | Outlet Temp. |  | 12.1356 |  | mm / mm ℃ / 10^6
38 | [6 empty] | αTa | at | Ambient Temp. |  | 11.52 |  | at | Ambient Temp. |  | 11.52 |  | mm / mm ℃ / 10^6
39 | Calculation Formula :
40 |  | Δ | = | L x ( αT x T - αTa x Ta ) | [5 empty] | Where, | L | Length |  | mm | T | Temp., Oper, Inlet or Outlet |  |  |  | ℃
41 | [10 empty] | Δ | Elongation |  | mm
42 | Point | SS | Δx | = | 2500 |  | x ( | 12.4809 | x | 158.286 | - | 11.52 | x | 10 | ) / 10^6 |  | = | 4.6509 |  | mm
43 |  |  | Δz | = | 0 |  | x ( | 12.4809 | x | 158.286 | - | 11.52 | x | 10 | ) / 10^6 |  | = | 0 |  | mm
44 | Point | N1 | Δx | = | 1400 |  | x ( | 12.4809 | x | 158.286 | - | 11.52 | x | 10 | ) / 10^6 |  | = | 2.6045 |  | mm
45 |  |  | Δz | = | 2124 |  | x ( | 12.4809 | x | 158.286 | - | 11.52 | x | 10 | ) / 10^6 |  | = | 3.9514 |  | mm
46 | Point | N2 | Δx | = | 3500 |  | x ( | 12.4809 | x | 158.286 | - | 11.52 | x | 10 | ) / 10^6 |  | = | 6.5112 |  | mm
47 |  |  | Δz | = | 2124 |  | x ( | 12.4809 | x | 158.286 | - | 11.52 | x | 10 | ) / 10^6 |  | = | 3.9514 |  | mm
48 | Point | N3 | Δx | = | -530 |  | x ( | 12.4809 | x | 158.286 | - | 11.52 | x | 10 | ) / 10^6 |  | = | -0.98599 |  | mm
49 |  |  | Δz | = | -300 |  | x ( | 12.4809 | x | 158.286 | - | 11.52 | x | 10 | ) / 10^6 |  | = | -0.55811 |  | mm
50 |  |  | Δxs | = | -900 |  | x ( | 12.4809 | x | 158.286 | - | 11.52 | x | 10 | ) / 10^6 |  | = | -1.6743 |  | mm
51 | Point | N4 | Δxc | = | -710 |  | x ( | 11.8764 | x | 65 | - | 11.52 | x | 10 | ) / 10^6 |  | = | -0.4663 |  | mm
52 |  |  | Δx | = | Δxs | + | Δxc | [9 empty] | = | -2.1406 |  | mm
53 |  |  | Δz | = | -300 |  | x ( | 11.8764 | x | 65 | - | 11.52 | x | 10 | ) / 10^6 |  | = | -0.19703 |  | mm
54 |  |  | Δxs | = | -900 |  | x ( | 12.4809 | x | 158.286 | - | 11.52 | x | 10 | ) / 10^6 |  | = | -1.6743 |  | mm
55 |  |  | Δxc | = | -710 |  | x ( | 12.1356 | x | 105 | - | 11.52 | x | 10 | ) / 10^6 |  | = | -0.82292 |  | mm
56 | Point | N5 | Δx | = | Δxs | + | Δxc | [9 empty] | = | -2.4972 |  | mm
57 |  |  | Δzci | = | 815 |  | x ( | 11.8764 | x | 65 | - | 11.52 | x | 10 | ) / 10^6 |  | = | 0.53526 |  | mm
58 |  |  | Δzco | = | 1115 |  | x ( | 12.1356 | x | 105 | - | 11.52 | x | 10 | ) / 10^6 |  | = | 1.2923 |  | mm
59 |  |  | Δz | = | Δzci | + | Δzco | [9 empty] | = | 1.8276 |  | mm
60 | Notes
61 | *1)
62 | *2)
63 | *3)
| NTES | [18 empty] | Narai Thermal Enginering Services
"Z"
"X"
Origin of Coordinate
Fixed Side
Sliding Side

## _Reaction Force
C A L C U L A T I O N o f T H E R M A L E X P A N S I O N
1 | Project |  |  | Gangnam CCPP | [10 empty] | Job No. |  | Later
2 | Client |  |  | KDHC | [10 empty] | Doc. No. |  | CAL - TERF - 100 | [5 empty] | Steam
3 | Contractor |  |  | Won Plant Co., Ltd. | [10 empty] | Date |  | 2015. 1. 10. | [5 empty] | Sat.
4 | [14 empty] | Revision |  | 0 | 1 |  |  |  |  | 5 | kg/cm2.g |  | 158.286 | < Tsat.
5 | Service of Unit |  |  | Turbine By-pass H/E | [10 empty] | Item No. |  | 112-M-HE-003 | [5 empty] | 158.286 |  |  | 250 | < TSH
6 | D E S I G N D A T A
7 | Shell Side | [9 empty] | Tube Side | [11 empty] | Shell Side |  | Tube Side
8 | Fluid Name |  |  |  |  | Steam |  |  |  |  | Fluid Name |  |  |  |  | DH Water |  |  |  |  | Fluid Kind |  | Saturated
9 | Inlet Press. |  |  |  |  | 5 |  |  | kg/cm2.g |  | Inlet Temp. |  |  | Ti | = | 65 |  |  | ℃ |  | Fluid in DB |  | H2O
10 | Inlet Temp. |  |  | To | = | 158.286 |  |  | ℃ |  | Outlet Temp. |  |  | To | = | 105 |  |  | ℃
11 | Shell Material |  |  |  |  | A 516-70 |  |  |  |  | Channel Material |  |  |  |  | A 516-70 |  |  |  |  | Material |  | ASTM
12 | Ambinet Temp. |  |  | Ta | = | 10 |  |  | ℃ | [13 empty] | plate |  | plate
13 | A S S U M P T I O N f o r C A L C U L A T I O N
14 | 1. | Saddle expansion is not considered.
15 | 2. | Origin of coordinate is located at the point, where there is no movement.
16 | 3. | Mean coefficient of thermal expansion values are from TEMA, Table D-11 M.
17 | C A L C U L A T I O N R E S U L T
18 |  | R ( | 593168.2361 |  | -593168.2361 |  | ) |  | R ( | -752475.7344 |  | -752475.7344 |  | )
19 |  |  | Δ ( | -2.4972 | 1.8276 | ) |  |  |  | Δ ( | 2.6045 | 3.9514 | ) |  |  | *** | *** | *** | ***
20 |  |  | N5 ( | -1610 | 2027 | ) ID | t |  |  | N1 ( | 1400 | 2124 | ) ID | t |  | *** | *** | *** | ***
21 |  |  |  | N5 |  | 529 | 15 |  |  |  | N1 |  | 535 | 12 |  |  | ***
22 | 15 | t | 300 | [9 empty] | 300 | 12 | t |  |  |  | 0
23 | ID | OD | [6 empty] | 1400 |  |  |  |  | ID | OD |  | 0
24 | 1600 | 1630 | [11 empty] | 1800 | 1824
25 |  |  |  |  | 710 | 900
26
27 | [6 empty] | 530
28
29 |  |  | 300 |  |  | 300
30 |  |  |  | N4 |  |  | N3
31 |  |  | N4 ( | -1610 | -203 | ) N3 ( | -530 | -300 | ) | [6 empty] | SS
32 |  |  | Δ ( | -2.1406 | -0.19703 | ) Δ ( | -0.98599 | -0.55811 | ) | [5 empty] | SS ( | 2500 | 0 | )
33 | [10 empty] | 2500 |  |  |  | Δ ( | 4.6509 | 0 | )
34
35 | C A L C U L A T I O N D E T A I L
36 | [7 empty] | Shell Material |  |  |  |  | Channel Material
37 | Mean Coeff. of Thermal Expansion | [5 empty] | αT | at | Oper. Temp. |  | 12.4809 |  | at | Inlet Temp. |  | 11.8764 |  | mm / mm ℃ / 10^6
38 | [12 empty] | at | Outlet Temp. |  | 12.1356 |  | mm / mm ℃ / 10^6
39 | [6 empty] | αTa | at | Ambient Temp. |  | 11.52 |  | at | Ambient Temp. |  | 11.52 |  | mm / mm ℃ / 10^6
40 | Modulus of Elasticity | [5 empty] | E | at | Oper. Temp. |  | 1961459.4788 |  | at | Outlet Temp. |  | 1996366.0714 |  | kg/cm2
41 | Calculation Formula :
42 |  | Δ | = | L x ( αT x T - αTa x Ta ) | [5 empty] | Where, | Δ | Elongation |  | mm | T | Temp., Oper, Inlet or Outlet |  |  |  | ℃
43 | [10 empty] | L | Length |  | mm
44 |  | R | = | A x E x ( αT x T - αTa x Ta ) | [5 empty] | Where, | R | Reaction Force when constrained | [5 empty] | kg/cm2
45 | [10 empty] | A | Nozzle Section Area | [5 empty] | cm2
46 | Point | SS | Δx | = | 2500 |  | x ( | 12.4809 | x | 158.286 | - | 11.52 | x | 10 | ) / 10^6 |  | = | 4.6509 |  | mm
47 |  |  | Δz | = | 0 |  | x ( | 12.4809 | x | 158.286 | - | 11.52 | x | 10 | ) / 10^6 |  | = | 0 |  | mm
48 |  |  | Δx | = | 1400 |  | x ( | 12.4809 | x | 158.286 | - | 11.52 | x | 10 | ) / 10^6 |  | = | 2.6045 |  | mm | Point | N3 | Δx = | -530 | x ( | 12.4809 | x | 158.286 | - | 11.52 | x | 10 | ) / 10^6 = | -0.98599 | mm
49 | Point | N1 | Δz | = | 2124 |  | x ( | 12.4809 | x | 158.286 | - | 11.52 | x | 10 | ) / 10^6 |  | = | 3.9514 |  | mm |  |  | Δz = | -300 | x ( | 12.4809 | x | 158.286 | - | 11.52 | x | 10 | ) / 10^6 = | -0.55811 | mm
50 |  |  | Rx | = | 206.2141 |  | x | 1961459.4788 |  | x | ( αT x T - αTa x Ta ) |  |  |  | / 10^6 |  | = | -752475.7344 |  | kg/cm2
51 |  |  | Rz | = | 206.2141 |  | x | 1961459.4788 |  | x | ( αT x T - αTa x Ta ) |  |  |  | / 10^6 |  | = | -752475.7344 |  | kg/cm2
52 |  |  | Δxs | = | -900 |  | x ( | 12.4809 | x | 158.286 | - | 11.52 | x | 10 | ) / 10^6 |  | = | -1.6743 |  | mm |  |  | Δxs = | -900 | x ( | 12.4809 | x | 158.286 | - | 11.52 | x | 10 | ) / 10^6 = | -1.6743 | mm
53 |  |  | Δxc | = | -710 |  | x ( | 12.1356 | x | 105 | - | 11.52 | x | 10 | ) / 10^6 |  | = | -0.82292 |  | mm | Point | N4 | Δxc = | -710 | x ( | 11.8764 | x | 65 | - | 11.52 | x | 10 | ) / 10^6 = | -0.4663 | mm
54 |  |  | Δx | = | Δxs | + | Δxc | [9 empty] | = | -2.4972 |  | mm |  |  | Δx = | Δxs | + | Δxc | [7 empty] | -2.1406 | mm
55 | Point | N5 | Δzci | = | 815 |  | x ( | 11.8764 | x | 65 | - | 11.52 | x | 10 | ) / 10^6 |  | = | 0.53526 |  | mm |  |  | Δz = | -300 | x ( | 11.8764 | x | 65 | - | 11.52 | x | 10 | ) / 10^6 = | -0.19703 | mm
56 |  |  | Δzco | = | 1115 |  | x ( | 12.1356 | x | 105 | - | 11.52 | x | 10 | ) / 10^6 |  | = | 1.2923 |  | mm
57 |  |  | Δz | = | Δzci | + | Δzco | [9 empty] | = | 1.8276 |  | mm
58 |  |  | Rx | = | 256.354 |  | x | 1996366.0714 |  | x | ( αT x T - αTa x Ta ) |  |  |  | / 10^6 |  | = | 593168.2361 |  | kg/cm2
59 |  |  | Rz | = | 256.354 |  | x | 1996366.0714 |  | x | ( αT x T - αTa x Ta ) |  |  |  | / 10^6 |  | = | -593168.2361 |  | kg/cm2
60 | Notes
61 | *1)
62 | *2)
| NTES | [18 empty] | Narai Thermal Enginering Services
"Z"
"X"
Origin of Coordinate
Fixed Side
Sliding Side

## LP #1
C A L C U L A T I O N o f T H E R M A L E X P A N S I O N
1 | Project |  |  | Paco Power Plant Project | [10 empty] | Job No. |  | 11217D
2 | Client |  |  | Minera Panama S.A | [10 empty] | Doc. No. |  | CAL - TEXP - 100 |  |  |  |  | Steam
3 | Contractor |  |  | SK E&C | [10 empty] | Date |  | 2014. 1. 1. |  |  |  |  | Sat.
4 | [14 empty] | Revision |  | 0 |  |  |  |  | -0.45225 | bar.g | 84.2108 | < Tsat.
5 | Service of Unit |  |  | LP Heater #1 | [10 empty] | Item No. |  | 1CD003A, 2CD003A |  |  |  |  | 84.2108 |  | 250 | < TSH
6 | D E S I G N D A T A
7 | Shell Side | [9 empty] | Tube Side | [10 empty] | Shell Side |  |  | Tube Side
8 | Fluid Name |  |  |  |  | Steam |  |  |  |  | Fluid Name |  |  |  |  | Condensate |  |  |  |  | Fluid Kind | Saturated
9 | Inlet Press. |  |  |  |  | -0.45225 | / | 0.561 | bar.g | / bar.a | Inlet Temp. |  |  | Ti | = | 41.36 |  |  | ℃ |  | Fluid in DB | H2O
10 | Inlet Temp. |  |  | Ti | = | 84.2108 |  |  | ℃ |  | Outlet Temp. |  |  | To | = | 81.22 |  |  | ℃
11 | Shell Material |  |  |  |  | A 516-70 |  |  |  |  | Channel Material |  |  |  |  | A 516-70 |  |  |  |  | Material | ASTM
12 | Ambinet Temp. |  |  | Ta | = | 10 |  |  | ℃ | [12 empty] | plate |  |  | plate
13 | A S S U M P T I O N f o r C A L C U L A T I O N
14 | 1. | Saddle expansion is not considered.
15 | 2. | Origin of coordinate is located at the point, where there is no movement.
16 | 3. | Mean coefficient of thermal expansion values are from TEMA, Table D-11 M.
17 | C A L C U L A T I O N R E S U L T
18 |  |  | Δ ( | -5.2775 | 0.70505 | ) |  |  | Δ ( | -1.8803 | 1.0387 | ) | Δ ( | 1.8803 | 1.0387 | ) | Δ ( | 5.6894 | 1.0387 | )
19 |  |  | B ( | -5906 | 1124.5 | ) |  |  | C2 ( | -2100 | 1160 | ) | C1 ( | 2100 | 1160 | ) | D ( | 6354 | 1160 | )
20 |  |  |  | B | [5 empty] | C2 |  |  | C1 |  |  |  |  | D
21 | 25 | t | 150 | [8 empty] | 150 |  |  | 10 | t |  |  |  | 150
22 | ID | OD | [6 empty] | -2100 |  |  | 4200 |  |  | ID | OD |  | 600
23 | 889 | 939 | [12 empty] | 990 | 1010
24 |  |  |  |  | 286 | 5620
25
26 | [6 empty] | 5370
27
28 |  |  | 150 |  |  | 150 | [12 empty] | 150
29 |  |  |  | A |  |  | E | [5 empty] | 5754 |  |  |  | F
30 |  |  | A ( | -5906 | -114.5 | ) E ( | -5370 | -150 | ) | [6 empty] | F ( | 5754 | -150 | )
31 |  |  | Δ ( | -5.1379 | -0.055451 | ) Δ ( | -4.8083 | -0.13431 | ) | [6 empty] | Δ ( | 5.1522 | -0.13431 | )
32
33
34 | C A L C U L A T I O N D E T A I L
35 | [7 empty] | Shell Material |  |  |  |  | Channel Material
36 | Mean Coeff. of Thermal Expansion | [5 empty] | αT | at | Oper. Temp. |  | 12.0009 |  | at | Inlet Temp. |  | 11.7232 |  | mm / mm ℃ / 10^6
37 | [12 empty] | at | Outlet Temp. |  | 11.9815 |  | mm / mm ℃ / 10^6
38 | [6 empty] | αTa | at | Ambient Temp. |  | 11.52 |  | at | Ambient Temp. |  | 11.52 |  | mm / mm ℃ / 10^6
39 | Calculation Formula :
40 |  | Δ | = | L x ( αT x T - αTa x Ta ) | [5 empty] | Where, | L | Length |  | mm | T | Temp., Oper, Inlet or Outlet |  |  |  | ℃
41 | [10 empty] | Δ | Elongation |  | mm
42 | Point | C2 | Δx | = | -2100 |  | x ( | 12.0009 | x | 84.2108 | - | 11.52 | x | 10 | ) / 10^6 |  | = | -1.8803 |  | mm
43 |  |  | Δz | = | 1160 |  | x ( | 12.0009 | x | 84.2108 | - | 11.52 | x | 10 | ) / 10^6 |  | = | 1.0387 |  | mm
44 | Point | C1 | Δx | = | 2100 |  | x ( | 12.0009 | x | 84.2108 | - | 11.52 | x | 10 | ) / 10^6 |  | = | 1.8803 |  | mm
45 |  |  | Δz | = | 1160 |  | x ( | 12.0009 | x | 84.2108 | - | 11.52 | x | 10 | ) / 10^6 |  | = | 1.0387 |  | mm
46 | Point | D | Δx | = | 6354 |  | x ( | 12.0009 | x | 84.2108 | - | 11.52 | x | 10 | ) / 10^6 |  | = | 5.6894 |  | mm
47 |  |  | Δz | = | 1160 |  | x ( | 12.0009 | x | 84.2108 | - | 11.52 | x | 10 | ) / 10^6 |  | = | 1.0387 |  | mm
48 | Point | F | Δx | = | 5754 |  | x ( | 12.0009 | x | 84.2108 | - | 11.52 | x | 10 | ) / 10^6 |  | = | 5.1522 |  | mm
49 |  |  | Δz | = | -150 |  | x ( | 12.0009 | x | 84.2108 | - | 11.52 | x | 10 | ) / 10^6 |  | = | -0.13431 |  | mm
50 | Point | E | Δx | = | -5370 |  | x ( | 12.0009 | x | 84.2108 | - | 11.52 | x | 10 | ) / 10^6 |  | = | -4.8083 |  | mm
51 |  |  | Δz | = | -150 |  | x ( | 12.0009 | x | 84.2108 | - | 11.52 | x | 10 | ) / 10^6 |  | = | -0.13431 |  | mm
52 |  |  | Δxs | = | -5620 |  | x ( | 12.0009 | x | 84.2108 | - | 11.52 | x | 10 | ) / 10^6 |  | = | -5.0322 |  | mm
53 | Point | A | Δxc | = | -286 |  | x ( | 11.7232 | x | 41.36 | - | 11.52 | x | 10 | ) / 10^6 |  | = | -0.10573 |  | mm
54 |  |  | Δx | = | Δxs | + | Δxc | [9 empty] | = | -5.1379 |  | mm
55 |  |  | Δz | = | -150 |  | x ( | 11.7232 | x | 41.36 | - | 11.52 | x | 10 | ) / 10^6 |  | = | -0.055451 |  | mm
56 |  |  | Δxs | = | -5620 |  | x ( | 12.0009 | x | 84.2108 | - | 11.52 | x | 10 | ) / 10^6 |  | = | -5.0322 |  | mm
57 |  |  | Δxc | = | -286 |  | x ( | 11.9815 | x | 81.22 | - | 11.52 | x | 10 | ) / 10^6 |  | = | -0.24537 |  | mm
58 | Point | B | Δx | = | Δxs | + | Δxc | [9 empty] | = | -5.2775 |  | mm
59 |  |  | Δzci | = | 469.5 |  | x ( | 11.7232 | x | 41.36 | - | 11.52 | x | 10 | ) / 10^6 |  | = | 0.17356 |  | mm
60 |  |  | Δzco | = | 619.5 |  | x ( | 11.9815 | x | 81.22 | - | 11.52 | x | 10 | ) / 10^6 |  | = | 0.53149 |  | mm
61 |  |  | Δz | = | Δzci | + | Δzco | [9 empty] | = | 0.70505 |  | mm
62 | Notes
63 | *1)
64 | *2)
65 | *3)
| NTES | [18 empty] | Narai Thermal Enginering Services
"Z"
"X"
Origin of Coordinate
Fixed Side
Sliding Side
Fixed Side

## LP #3
C A L C U L A T I O N o f T H E R M A L E X P A N S I O N
1 | Project |  |  | Paco Power Plant Project | [10 empty] | Job No. |  | 11217D
2 | Client |  |  | Minera Panama S.A | [10 empty] | Doc. No. |  | CAL - TEXP - 100 |  |  |  |  | Steam
3 | Contractor |  |  | SK E&C | [10 empty] | Date |  | 2014. 1. 1. |  |  |  |  | S/H
4 | [14 empty] | Revision |  | 0 |  |  |  |  | 3.5238 | bar.g | 148.2105 | < Tsat.
5 | Service of Unit |  |  | LP Heater #3 | [10 empty] | Item No. |  | 1CD005A, 2CD005A |  |  |  |  | 263.15 |  | 263.15 | < TSH
6 | D E S I G N D A T A
7 | Shell Side | [9 empty] | Tube Side | [10 empty] | Shell Side |  |  | Tube Side
8 | Fluid Name |  |  |  |  | Steam |  |  |  |  | Fluid Name |  |  |  |  | Condensate |  |  |  |  | Fluid Kind | Saturated
9 | Inlet Press. |  |  |  |  | 3.5238 | / | 4.537 | bar.g | / bar.a | Inlet Temp. |  |  | Ti | = | 102.09 |  |  | ℃ |  | Fluid in DB | H2O
10 | Inlet Temp. |  |  | Ti | = | 263.15 |  |  | ℃ |  | Outlet Temp. |  |  | To | = | 145.24 |  |  | ℃
11 | Shell Material |  |  |  |  | A 516-70 |  |  |  |  | Channel Material |  |  |  |  | A 516-70 |  |  |  |  | Material | ASTM
12 | Ambinet Temp. |  |  | Ta | = | 10 |  |  | ℃ | [12 empty] | plate |  |  | plate
13 | A S S U M P T I O N f o r C A L C U L A T I O N
14 | 1. | Saddle expansion is not considered.
15 | 2. | Origin of coordinate is located at the point, where there is no movement.
16 | 3. | Mean coefficient of thermal expansion values are from TEMA, Table D-11 M.
17 | C A L C U L A T I O N R E S U L T
18 |  |  | Δ ( | 0 | 1.3924 | ) |  |  | Δ ( | 19.24 | 3.4596 | ) | Δ ( | *** | *** | ) | *** | *** | *** | ***
19 |  |  | B ( | 0 | 998.5 | ) |  |  | C ( | 5756 | 1035 | ) | *** ( | *** | *** | ) | *** | *** | *** | ***
20 |  |  |  | B | [5 empty] | C |  |  | *** |  |  |  |  | ***
21 | 25 | t | 150 | [8 empty] | 150 |  |  | 10 | t |  |  |  | 0
22 | ID | OD | [6 empty] | 5756 |  |  | 0 |  |  | ID | OD |  | 0
23 | 762 | 812 | [12 empty] | 865 | 885
24 |  |  |  |  | 286 | -286
25
26 | [6 empty] | -571
27
28 |  |  | 150 |  |  | 150 | [12 empty] | 150
29 |  |  |  | A |  |  | E | [5 empty] | 6756 |  |  |  | F
30 |  |  | A ( | 0 | -113.5 | ) E ( | 571 | -150 | ) | [6 empty] | F ( | 6756 | -150 | )
31 |  |  | Δ ( | 0 | -0.16827 | ) Δ ( | 1.9086 | -0.50139 | ) | [6 empty] | Δ ( | 22.5825 | -0.50139 | )
32
33
34 | C A L C U L A T I O N D E T A I L
35 | [7 empty] | Shell Material |  |  |  |  | Channel Material
36 | Mean Coeff. of Thermal Expansion | [5 empty] | αT | at | Oper. Temp. |  | 13.14 |  | at | Inlet Temp. |  | 12.1167 |  | mm / mm ℃ / 10^6
37 | [12 empty] | at | Outlet Temp. |  | 12.3964 |  | mm / mm ℃ / 10^6
38 | [6 empty] | αTa | at | Ambient Temp. |  | 11.52 |  | at | Ambient Temp. |  | 11.52 |  | mm / mm ℃ / 10^6
39 | Calculation Formula :
40 |  | Δ | = | L x ( αT x T - αTa x Ta ) | [5 empty] | Where, | L | Length |  | mm | T | Temp., Oper, Inlet or Outlet |  |  |  | ℃
41 | [10 empty] | Δ | Elongation |  | mm
42 | Point | C | Δx | = | 5756 |  | x ( | 13.14 | x | 263.15 | - | 11.52 | x | 10 | ) / 10^6 |  | = | 19.24 |  | mm
43 |  |  | Δz | = | 1035 |  | x ( | 13.14 | x | 263.15 | - | 11.52 | x | 10 | ) / 10^6 |  | = | 3.4596 |  | mm
44 | Point | *** | Δx | = | *** |  | x ( | 13.14 | x | 263.15 | - | 11.52 | x | 10 | ) / 10^6 |  | = | *** |  | mm
45 |  |  | Δz | = | *** |  | x ( | 13.14 | x | 263.15 | - | 11.52 | x | 10 | ) / 10^6 |  | = | *** |  | mm
46 | Point | *** | Δx | = | *** |  | x ( | 13.14 | x | 263.15 | - | 11.52 | x | 10 | ) / 10^6 |  | = | *** |  | mm
47 |  |  | Δz | = | *** |  | x ( | 13.14 | x | 263.15 | - | 11.52 | x | 10 | ) / 10^6 |  | = | *** |  | mm
48 | Point | F | Δx | = | 6756 |  | x ( | 13.14 | x | 263.15 | - | 11.52 | x | 10 | ) / 10^6 |  | = | 22.5825 |  | mm
49 |  |  | Δz | = | -150 |  | x ( | 13.14 | x | 263.15 | - | 11.52 | x | 10 | ) / 10^6 |  | = | -0.50139 |  | mm
50 | Point | E | Δx | = | 571 |  | x ( | 13.14 | x | 263.15 | - | 11.52 | x | 10 | ) / 10^6 |  | = | 1.9086 |  | mm
51 |  |  | Δz | = | -150 |  | x ( | 13.14 | x | 263.15 | - | 11.52 | x | 10 | ) / 10^6 |  | = | -0.50139 |  | mm
52 |  |  | Δxs | = | 286 |  | x ( | 12.1167 | x | 102.09 | - | 11.52 | x | 10 | ) / 10^6 |  | = | 0.32083 |  | mm
53 | Point | A | Δxc | = | -286 |  | x ( | 12.1167 | x | 102.09 | - | 11.52 | x | 10 | ) / 10^6 |  | = | -0.32083 |  | mm
54 |  |  | Δx | = | Δxs | + | Δxc | [9 empty] | = | 0 |  | mm
55 |  |  | Δz | = | -150 |  | x ( | 12.1167 | x | 102.09 | - | 11.52 | x | 10 | ) / 10^6 |  | = | -0.16827 |  | mm
56 |  |  | Δxs | = | 286 |  | x ( | 12.3964 | x | 145.24 | - | 11.52 | x | 10 | ) / 10^6 |  | = | 0.48198 |  | mm
57 |  |  | Δxc | = | -286 |  | x ( | 12.3964 | x | 145.24 | - | 11.52 | x | 10 | ) / 10^6 |  | = | -0.48198 |  | mm
58 | Point | B | Δx | = | Δxs | + | Δxc | [9 empty] | = | 0 |  | mm
59 |  |  | Δzci | = | 406 |  | x ( | 12.1167 | x | 102.09 | - | 11.52 | x | 10 | ) / 10^6 |  | = | 0.45545 |  | mm
60 |  |  | Δzco | = | 556 |  | x ( | 12.3964 | x | 145.24 | - | 11.52 | x | 10 | ) / 10^6 |  | = | 0.937 |  | mm
61 |  |  | Δz | = | Δzci | + | Δzco | [9 empty] | = | 1.3924 |  | mm
62 | Notes
63 | *1)
64 | *2)
65 | *3)
| NTES | [18 empty] | Narai Thermal Enginering Services
"Z"
"X"
Origin of Coordinate
Fixed Side
Sliding Side
Fixed Side

## HP #5
C A L C U L A T I O N o f T H E R M A L E X P A N S I O N
1 | Project |  |  | Paco Power Plant Project | [10 empty] | Job No. |  | 11217D
2 | Client |  |  | Minera Panama S.A | [10 empty] | Doc. No. |  | CAL - TEXP - 100 |  |  |  |  | Steam
3 | Contractor |  |  | SK E&C | [10 empty] | Date |  | 2014. 1. 1. |  |  |  |  | Sat.
4 | [14 empty] | Revision |  | 0 |  |  |  |  | 25.2968 | bar.g | 226.6887 | < Tsat.
5 | Service of Unit |  |  | HP Heater #5 | [10 empty] | Item No. |  | 1FW001A, 2FW001A |  |  |  |  | 226.6887 |  | 0 | < TSH
6 | D E S I G N D A T A
7 | Shell Side | [9 empty] | Tube Side | [10 empty] | Shell Side |  |  | Tube Side
8 | Fluid Name |  |  |  |  | Steam |  |  |  |  | Fluid Name |  |  |  |  | Feed Water |  |  |  |  | Fluid Kind | Saturated
9 | Inlet Press. |  |  |  |  | 25.2968 | / | 26.31 | bar.g | / bar.a | Inlet Temp. |  |  | Ti | = | 195.96 |  |  | ℃ |  | Fluid in DB | H2O
10 | Oper. Temp., Sat. |  |  | To | = | 226.6887 |  |  | ℃ |  | Outlet Temp. |  |  | To | = | 226.69 |  |  | ℃
11 | Shell Material |  |  |  |  | A 516-70N |  |  |  |  | Channel Material |  |  |  |  | A 516-70 |  |  |  |  | Material | ASTM
12 | Ambinet Temp. |  |  | Ta | = | 10 |  |  | ℃ | [12 empty] | plate |  |  | plate
13 | A S S U M P T I O N f o r C A L C U L A T I O N
14 | 1. | Saddle expansion is not considered.
15 | 2. | Origin of coordinate is located at the point, where there is no movement.
16 | 3. | Mean coefficient of thermal expansion values are from TEMA, Table D-11 M.
17 | C A L C U L A T I O N R E S U L T
18 |  |  | Δ ( | -1.6747 | 3.4323 | ) |  |  | Δ ( | 1.2947 | 3.5266 | ) | Δ ( | *** | *** | ) | Δ ( | 31.3767 | 3.5266 | )
19 |  |  | B ( | -595 | 1304.9421 | ) |  |  | C ( | 460 | 1253 | ) | *** ( | *** | *** | ) | D ( | 11148 | 1253 | )
20 |  |  |  | B |  | 30 | deg |  |  | C |  |  | *** |  |  |  |  | D
21 | [11 empty] | 150 |  |  | 19 | t |  |  |  | 150
22 | [8 empty] | 460 |  |  | 0 |  |  | ID | OD |  | 3153
23 |  |  | 870 | [11 empty] | 1065 | 1103
24 | 1506.8842 |  |  |  | 435 | 160
25
26 | [6 empty] | -460
27
28 | [5 empty] | 150 | [12 empty] | 150
29 |  |  |  | A |  |  | E | [5 empty] | 7995 |  |  |  | F
30 |  |  | A ( | -595 | -201.9421 | ) E ( | 460 | -150 | ) | [6 empty] | F ( | 7995 | -150 | )
31 |  |  | Δ ( | -1.4849 | -0.4803 | ) Δ ( | 1.2947 | -0.42218 | ) | [6 empty] | Δ ( | 22.5024 | -0.42218 | )
32
33
34 | C A L C U L A T I O N D E T A I L
35 | [7 empty] | Shell Material |  |  |  |  | Channel Material
36 | Mean Coeff. of Thermal Expansion | [5 empty] | αT | at | Oper. Temp. |  | 12.9241 |  | at | Inlet Temp. |  | 12.725 |  | mm / mm ℃ / 10^6
37 | [12 empty] | at | Outlet Temp. |  | 12.9242 |  | mm / mm ℃ / 10^6
38 | [6 empty] | αTa | at | Ambient Temp. |  | 11.52 |  | at | Ambient Temp. |  | 11.52 |  | mm / mm ℃ / 10^6
39 | Calculation Formula :
40 |  | Δ | = | L x ( αT x T - αTa x Ta ) | [5 empty] | Where, | L | Length |  | mm | T | Temp., Oper, Inlet or Outlet |  |  |  | ℃
41 | [10 empty] | Δ | Elongation |  | mm
42 | Point | C | Δx | = | 460 |  | x ( | 12.9241 | x | 226.6887 | - | 11.52 | x | 10 | ) / 10^6 |  | = | 1.2947 |  | mm
43 |  |  | Δz | = | 1253 |  | x ( | 12.9241 | x | 226.6887 | - | 11.52 | x | 10 | ) / 10^6 |  | = | 3.5266 |  | mm
44 | Point | *** | Δx | = | *** |  | x ( | 12.9241 | x | 226.6887 | - | 11.52 | x | 10 | ) / 10^6 |  | = | *** |  | mm
45 |  |  | Δz | = | *** |  | x ( | 12.9241 | x | 226.6887 | - | 11.52 | x | 10 | ) / 10^6 |  | = | *** |  | mm
46 | Point | D | Δx | = | 11148 |  | x ( | 12.9241 | x | 226.6887 | - | 11.52 | x | 10 | ) / 10^6 |  | = | 31.3767 |  | mm
47 |  |  | Δz | = | 1253 |  | x ( | 12.9241 | x | 226.6887 | - | 11.52 | x | 10 | ) / 10^6 |  | = | 3.5266 |  | mm
48 | Point | F | Δx | = | 7995 |  | x ( | 12.9241 | x | 226.6887 | - | 11.52 | x | 10 | ) / 10^6 |  | = | 22.5024 |  | mm
49 |  |  | Δz | = | -150 |  | x ( | 12.9241 | x | 226.6887 | - | 11.52 | x | 10 | ) / 10^6 |  | = | -0.42218 |  | mm
50 | Point | E | Δx | = | 460 |  | x ( | 12.9241 | x | 226.6887 | - | 11.52 | x | 10 | ) / 10^6 |  | = | 1.2947 |  | mm
51 |  |  | Δz | = | -150 |  | x ( | 12.9241 | x | 226.6887 | - | 11.52 | x | 10 | ) / 10^6 |  | = | -0.42218 |  | mm
52 |  |  | Δxs | = | -160 |  | x ( | 12.9241 | x | 226.6887 | - | 11.52 | x | 10 | ) / 10^6 |  | = | -0.45033 |  | mm
53 | Point | A | Δxc | = | -435 |  | x ( | 12.725 | x | 195.96 | - | 11.52 | x | 10 | ) / 10^6 |  | = | -1.0346 |  | mm
54 |  |  | Δx | = | Δxs | + | Δxc | [9 empty] | = | -1.4849 |  | mm
55 |  |  | Δz | = | -201.9421 |  | x ( | 12.725 | x | 195.96 | - | 11.52 | x | 10 | ) / 10^6 |  | = | -0.4803 |  | mm
56 |  |  | Δxs | = | -160 |  | x ( | 12.9241 | x | 226.6887 | - | 11.52 | x | 10 | ) / 10^6 |  | = | -0.45033 |  | mm
57 |  |  | Δxc | = | -435 |  | x ( | 12.9242 | x | 226.69 | - | 11.52 | x | 10 | ) / 10^6 |  | = | -1.2243 |  | mm
58 | Point | B | Δx | = | Δxs | + | Δxc | [9 empty] | = | -1.6747 |  | mm
59 |  |  | Δzci | = | 551.5 |  | x ( | 12.725 | x | 195.96 | - | 11.52 | x | 10 | ) / 10^6 |  | = | 1.3117 |  | mm
60 |  |  | Δzco | = | 753.4421 |  | x ( | 12.9242 | x | 226.69 | - | 11.52 | x | 10 | ) / 10^6 |  | = | 2.1206 |  | mm
61 |  |  | Δz | = | Δzci | + | Δzco | [9 empty] | = | 3.4323 |  | mm
62 | Notes
63 | *1)
64 | *2)
65 | *3)
| NTES | [18 empty] | Narai Thermal Enginering Services
"Z"
"X"
Origin of Coordinate
Fixed Side
Sliding Side
Fixed Side

## HP #8
C A L C U L A T I O N o f T H E R M A L E X P A N S I O N
1 | Project |  |  | Paco Power Plant Project | [10 empty] | Job No. |  | 11217D
2 | Client |  |  | Minera Panama S.A | [10 empty] | Doc. No. |  | CAL - TEXP - 100 |  |  |  |  | Steam
3 | Contractor |  |  | SK E&C | [10 empty] | Date |  | 2014. 1. 1. |  |  |  |  | S/H
4 | [14 empty] | Revision |  | 0 |  |  |  |  | 25.2988 | bar.g | 226.6928 | < Tsat.
5 | Service of Unit |  |  | HP Heater #8 | [10 empty] | Item No. |  | 1FW004A, 2FW004A |  |  |  |  | 502.69 |  | 502.69 | < TSH
6 | D E S I G N D A T A
7 | Shell Side | [9 empty] | Tube Side | [10 empty] | Shell Side |  |  | Tube Side
8 | Fluid Name |  |  |  |  | Steam |  |  |  |  | Fluid Name |  |  |  |  | Feed Water |  |  |  |  | Fluid Kind | Saturated
9 | Inlet Press. |  |  |  |  | 25.2988 | / | 26.312 | bar.g | / bar.a | Inlet Temp. |  |  | Ti | = | 281.5 |  |  | ℃ |  | Fluid in DB | H2O
10 | Inlet Temp. |  |  | Ti | = | 502.69 |  |  | ℃ |  | Outlet Temp. |  |  | To | = | 286.45 |  |  | ℃
11 | Shell Material |  |  |  |  | A 516-70N |  |  |  |  | Channel Material |  |  |  |  | A 387 11 CL.2 |  |  |  |  | Material | ASTM
12 | Ambinet Temp. |  |  | Ta | = | 10 |  |  | ℃ | [12 empty] | plate |  |  | plate
13 | A S S U M P T I O N f o r C A L C U L A T I O N
14 | 1. | Saddle expansion is not considered.
15 | 2. | Origin of coordinate is located at the point, where there is no movement.
16 | 3. | Mean coefficient of thermal expansion values are from TEMA, Table D-11 M.
17 | C A L C U L A T I O N R E S U L T
18 |  |  | Δ ( | -2.5031 | 4.3725 | ) |  |  | Δ ( | 10.2449 | 7.4973 | ) | Δ ( | *** | *** | ) | *** | *** | *** | ***
19 |  |  | B ( | -564 | 1206.4421 | ) |  |  | C ( | 1443 | 1056 | ) | *** ( | *** | *** | ) | *** | *** | *** | ***
20 |  |  |  | B |  | 30 | deg |  |  | C |  |  | *** |  |  |  |  | ***
21 | [11 empty] | 150 |  |  | 32 | t |  |  |  | 0
22 | [8 empty] | 1443 |  |  | 0 |  |  | ID | OD |  | 0
23 |  |  | 870 | [11 empty] | 842 | 906
24 | 1506.8842 |  |  |  | 435 | 129
25
26 | [6 empty] | -450
27
28 | [5 empty] | 150 | [12 empty] | 0
29 |  |  |  | A |  |  | E | [5 empty] | 0 |  |  |  | ***
30 |  |  | A ( | -564 | -300.4421 | ) E ( | 450 | -150 | ) | [6 empty] | *** ( | *** | *** | )
31 |  |  | Δ ( | -2.4748 | -1.0767 | ) Δ ( | 3.1949 | -1.065 | ) | [6 empty] | Δ ( | *** | *** | )
32
33
34 | C A L C U L A T I O N D E T A I L
35 | [7 empty] | Shell Material |  |  |  |  | Channel Material
36 | Mean Coeff. of Thermal Expansion | [5 empty] | αT | at | Oper. Temp. |  | 14.3526 |  | at | Inlet Temp. |  | 13.14 |  | mm / mm ℃ / 10^6
37 | [12 empty] | at | Outlet Temp. |  | 13.14 |  | mm / mm ℃ / 10^6
38 | [6 empty] | αTa | at | Ambient Temp. |  | 11.52 |  | at | Ambient Temp. |  | 11.52 |  | mm / mm ℃ / 10^6
39 | Calculation Formula :
40 |  | Δ | = | L x ( αT x T - αTa x Ta ) | [5 empty] | Where, | L | Length |  | mm | T | Temp., Oper, Inlet or Outlet |  |  |  | ℃
41 | [10 empty] | Δ | Elongation |  | mm
42 | Point | C | Δx | = | 1443 |  | x ( | 14.3526 | x | 502.69 | - | 11.52 | x | 10 | ) / 10^6 |  | = | 10.2449 |  | mm
43 |  |  | Δz | = | 1056 |  | x ( | 14.3526 | x | 502.69 | - | 11.52 | x | 10 | ) / 10^6 |  | = | 7.4973 |  | mm
44 | Point | *** | Δx | = | *** |  | x ( | 14.3526 | x | 502.69 | - | 11.52 | x | 10 | ) / 10^6 |  | = | *** |  | mm
45 |  |  | Δz | = | *** |  | x ( | 14.3526 | x | 502.69 | - | 11.52 | x | 10 | ) / 10^6 |  | = | *** |  | mm
46 | Point | *** | Δx | = | *** |  | x ( | 14.3526 | x | 502.69 | - | 11.52 | x | 10 | ) / 10^6 |  | = | *** |  | mm
47 |  |  | Δz | = | *** |  | x ( | 14.3526 | x | 502.69 | - | 11.52 | x | 10 | ) / 10^6 |  | = | *** |  | mm
48 | Point | *** | Δx | = | *** |  | x ( | 14.3526 | x | 502.69 | - | 11.52 | x | 10 | ) / 10^6 |  | = | *** |  | mm
49 |  |  | Δz | = | *** |  | x ( | 14.3526 | x | 502.69 | - | 11.52 | x | 10 | ) / 10^6 |  | = | *** |  | mm
50 | Point | E | Δx | = | 450 |  | x ( | 14.3526 | x | 502.69 | - | 11.52 | x | 10 | ) / 10^6 |  | = | 3.1949 |  | mm
51 |  |  | Δz | = | -150 |  | x ( | 14.3526 | x | 502.69 | - | 11.52 | x | 10 | ) / 10^6 |  | = | -1.065 |  | mm
52 |  |  | Δxs | = | -129 |  | x ( | 14.3526 | x | 502.69 | - | 11.52 | x | 10 | ) / 10^6 |  | = | -0.91586 |  | mm
53 | Point | A | Δxc | = | -435 |  | x ( | 13.14 | x | 281.5 | - | 11.52 | x | 10 | ) / 10^6 |  | = | -1.5589 |  | mm
54 |  |  | Δx | = | Δxs | + | Δxc | [9 empty] | = | -2.4748 |  | mm
55 |  |  | Δz | = | -300.4421 |  | x ( | 13.14 | x | 281.5 | - | 11.52 | x | 10 | ) / 10^6 |  | = | -1.0767 |  | mm
56 |  |  | Δxs | = | -129 |  | x ( | 14.3526 | x | 502.69 | - | 11.52 | x | 10 | ) / 10^6 |  | = | -0.91586 |  | mm
57 |  |  | Δxc | = | -435 |  | x ( | 13.14 | x | 286.45 | - | 11.52 | x | 10 | ) / 10^6 |  | = | -1.5872 |  | mm
58 | Point | B | Δx | = | Δxs | + | Δxc | [9 empty] | = | -2.5031 |  | mm
59 |  |  | Δzci | = | 453 |  | x ( | 13.14 | x | 281.5 | - | 11.52 | x | 10 | ) / 10^6 |  | = | 1.6234 |  | mm
60 |  |  | Δzco | = | 753.4421 |  | x ( | 13.14 | x | 286.45 | - | 11.52 | x | 10 | ) / 10^6 |  | = | 2.7491 |  | mm
61 |  |  | Δz | = | Δzci | + | Δzco | [9 empty] | = | 4.3725 |  | mm
62 | Notes
63 | *1)
64 | *2)
65 | *3)
| NTES | [18 empty] | Narai Thermal Enginering Services
"Z"
"X"
Origin of Coordinate
Fixed Side
Sliding Side
Fixed Side

## a
D E S I G N I N F O R M A T I O N
1 | Project | #NAME? | Job No. | #NAME?
2 | Client | #NAME? | Doc. No. | DI - AAA - 100
3 | Contractor | #NAME? | Date | 2007. 1. 15.
4 | Code/Standard | #NAME? | Revision | 0
5 | Service of Unit | #NAME? | Item No. | #NAME?
6 | Type | #NAME?
7
8 | A A A A A
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25 | A A A A A
26
27
28
29
30
31
32
33
34
35
36
37
38
39
40 | A A A A A
41
42
43
44
45
46
47
48
49
50
51
52
53
54
55 | Notes
56 | *1)
57 | *2)
58 | *3)
59 | *4)
60 | *5)
| #NAME? |  |  |  | #NAME?